## Slide 1: Performance Gap
Progress Report
Ying He
21 June

## Slide 2: Tasks
Create building models
Compare Standardized model and detailed dynamic models
Evaluate sources of modelling errors
Find out limitations of the standardized method
Identify the important parameters in modelling

## Slide 3: DesignBuilder Model
Honggerstrasse Residential Building

## Slide 4: DesignBuilder Model
Sumatrastrasse Office Building

## Slide 5: Norminal (Standardized) Analysis - EnergyPlus
SIA 2024 Building Schedule
SIA 382 Standardize building assumption

## Slide 6: Nominal Analysis Result
EnergyPlus heating energy demand much lower than the real measurement
Building | Real/Measurement Heating Demand (2015) (kWh/m2) | Calculated Heating Demand from EnergyPlus (kWh/m2) | % of calculated value to real heating demand
Sumatrastr. Office | 70 | 50.87 | 73%
Honggerstr. Residential | 62 | 36.22 | 60%
Chart: Comparison between simulation and measurement heating demand
| Honggerstr. Residential | Sumatrastr. Office
Calculated Heating Demand from EnergyPlus (kWh/m2) | 40.3 | 50.87
Real/Measurement Heating Demand (2015) (kWh/m2) | 62 | 70

## Slide 7: Dynamic Analysis – jE-Plus
Random generated parameters
Variable occupancy for different floors and zones (discrete)
Triangle distribution for heating, cooling, electricity, and lighting levels
Normal distribution for ventilation level
1000 jobs in total

## Slide 8: Honggerstr. Residential building results
Range between 31.07 to 42.05, lower than the measured heating demand

## Slide 9: Possible Reasons
Too low air infiltration (0.1)
Outdoor temperature limitation (default 0 degree)
Too low occupancy (average ~0.5 person per zone)
No window shading control
Too few time step
  A time step = 6 can obtain a higher heating demand than time step = 2 (origin)
Roughness parameter of insulation material
  Energy demand would obtain a higher value when insulation material has smooth surface
Different Weather Condition in 2015

## Slide 10: Heating demand with different air infiltration
Chart: Annual Heating Demand in Different Air Infiltration
| 0.1 | 0.2 | 0.3 | 0.4 | Measured Demand
Residential Building (Honggerstr) (kWh/m2) | 36.22 | 43.11 | 50.19 | 57.41 | 62
Office Building (Sumatrast) (kwh/m2) | 50.87 | 56.94 | 63.21 | 69.65 | 70

## Slide 11: Variable results with different infiltration (Sumatrastr)
Median: 63.39
Average: 63.54
> 70: 4.5%

## Slide 12: Variable results with different infiltration (Sumatrastr)
Median: 69.82
Average: 69.98
> 70 : 48.2%

## Slide 13: Variable results with different infiltration (Hongg)
Infiltration | Minimum heating demand (kWh/m2) | Nominal heating demand (kWh/m2) | Maximum heating demand (kWh/m2)
0.1 (standard) | 32.46 | 31.07 | 42.05
0.2 | 36.3 | 43.11 | 50.6
0.3 | 40.3 | 50.19 | 60.3
0.4 | 47.33 | 57.41 | 72.03
Median:57.46
Average:57.39
> 62 : 9.1%

## Slide 14: Annual Heating demand with different air infiltration & correct outdoor air temperature limitation (Hongger)
Air Infiltration | with outdoor air correction (kWh/m2) | without correction (kwh/m2)
0.1 (Standard) | 40.3 | 36.22
0.2 | 47.2 | 43.11
0.3 | 54.29 | 50.19
0.4 | 61.51 | 57.41
Measured value (2015) | 62 | 62
*Time step: 6
*Roughness of insulation material: smooth
Chart: Annual Heating Demand in Different Air Infiltration with Outdoor Air Correction (Honggerstr)
| 0.1 | 0.2 | 0.3 | 0.4 | REFERENCE (Measured)
Residential (Honggerstr) with outdoor air correction (kWh/m2) | 40.3 | 47.2 | 54.29 | 61.51 | 62
Residential (Honggerstr) without correction (kwh/m2) | 36.22 | 43.11 | 50.19 | 57.41 | 62

## Slide 15: Dynamic Analysis with Corrected outdoor air (Hongg)
Median: 61
Average: 60.95
> 62 : 40.4%

## Slide 16: Next Step
Redo the simulations in 2015 Zurich Weather file
  Replace the RH,wetbulb and drybulb temperature, wind speed with 2015 data
Review the building model/schedules